## zones
walls | 215B Office | 207 Conference | 209 Breakroom
n_occ | 1 | 20 | 24
floor_m2 | 12 | 70 | 34
12h_wlex1_m2
12h_wlex2_m2
12h_wd1_m2
12h_wd2_m2
6h_wlex1_m2 | 2.79 |  | 2.79
6h_wlex2_m2 | 5.5696 |  | 5.5696
6h_wd1_m2
6h_wd2_m2 | 3.7245 |  | 3.7245
3h_wlex1_m2 |  |  | 9.75
3h_wlex2_m2 |  |  | 16.7087
3h_wd1_m2
3h_wd2_m2 |  |  | 11.1735
9h_wlex1_m2 | 2.79
9h_wlex2_m2 | 5.5696
9h_wd1_m2
9h_wd2_m2 | 3.7245
roof_m2 | 12 | 70 | 34
flad_m2 | 12 | 70 | 34
wlad_m2 | 0 | 0 | 0
flin_m2 | 0 | 0 | 0
wlin_m2 | 0 | 0 | 0

## walls
parameters | wlex1 | wlex2 | roof | flad | wlad | flin | wlin
U_Wm2K | 0.24 | 0.24 | 0.18 | 2.55 | 0.6
mt_kgm2 | 533 | 28 | 56.8 | 312 | 9 | 312 | 9
mi_kgm2 | 13 | 13 | 10

## windows
parameters | wd1 | wd2
U_Wm2K | 1.8 | 1.8
g_gl | 0.49 | 0.49
f_fr | 0.1 | 0.1
H_B | 1 | 1
A1_deg | 18 | 18
A2_deg | 30 | 70
A3_deg
D_H

## general
parameters | value
azimuth_12h_deg | 180
h_ceiling_m | 2.74
n_infiltr_per_h | 0
internal_blind | 0
suspended_ceiling | 1
raised_floor | 0
carpet | 1
month | 7
t_in_C | 26
t_adj_C | 30
plant_start_h | 7
plant_stop_h | 23
occ_start_h | 7
occ_stop_h | 23
occ_rad_W | 60
occ_conv_W | 30
appliances_Wm2 | 10
lighting_rad_Wm2 | 2.4
lighting_conv_Wm2 | 2.4
lighting_factor | 0.8
roof_factor | 0.7
alpha_wall | 0.6
alpha_roof | 0.9
opaque_wall_shading | 0

## zones comments
walls | 215B Office | 207 Conference | 209 Breakroom
n_occ | 1 | 20 | 24 | Number of occupants per zone
floor_m2 | 12 | 70 | 34 | Floor area [m²]
12h_wlex1_m2 |  |  |  | Area of external wall type 1 with orientation 12h [m²]
12h_wlex2_m2 |  |  |  | Area of external wall type 2 with orientation 12h [m²]
12h_wd1_m2 |  |  |  | Area of external window type 1 with orientation 12h [m²]
12h_wd2_m2 |  |  |  | Area of external window type 2 with orientation 12h [m²]
6h_wlex1_m2 | 2.79 |  | 2.79 | Area of external wall type 1 with orientation 6h [m²]
6h_wlex2_m2 | 5.5696 |  | 5.5696 | Area of external wall type 2 with orientation 6h [m²]
6h_wd1_m2 |  |  |  | Area of external window type 1 with orientation 6h [m²]
6h_wd2_m2 | 3.7245 |  | 3.7245 | Area of external window type 2 with orientation 6h [m²]
3h_wlex1_m2 |  |  | 9.75 | Area of external wall type 1 with orientation 3h [m²]
3h_wlex2_m2 |  |  | 16.7087 | Area of external wall type 2 with orientation 3h [m²]
3h_wd1_m2 |  |  |  | Area of external window type 1 with orientation 3h [m²]
3h_wd2_m2 |  |  | 11.1735 | Area of external window type 2 with orientation 3h [m²]
9h_wlex1_m2 | 2.79 |  |  | Area of external wall type 1 with orientation 9h [m²]
9h_wlex2_m2 | 5.5696 |  |  | Area of external wall type 2 with orientation 9h [m²]
9h_wd1_m2 |  |  |  | Area of external window type 1 with orientation 9h [m²]
9h_wd2_m2 | 3.7245 |  |  | Area of external window type 2 with orientation 9h [m²]
roof_m2 | 12 | 70 | 34 | Roof area [m²]
flad_m2 | 12 | 70 | 34 | Internal wall area adjacent to unconditioned zone [m²]
wlad_m2 | 0 | 0 | 0 | Internal floor area adjacent to unconditioned zone [m²]
flin_m2 | 0 | 0 | 0 | Internal wall area adjacent to conditioned zone [m²]
wlin_m2 | 0 | 0 | 0 | Internal floor area adjacent to conditioned zone [m²]

## walls comments
parameters | wlex1 | wlex2 | roof | flad | wlad | flin | wlin
U_Wm2K | 0.24 | 0.24 | 0.18 | 2.55 | 0.6
mt_kgm2 | 533 | 28 | 56.8 | 312 | 9 | 312 | 9
mi_kgm2 | 13 | 13 | 10

## windows comments
parameters | wd1 | wd2
U_Wm2K | 1.8 | 1.8 | U_value [W/m²K]
g_gl | 0.49 | 0.49 | Glazing Solar Factor
f_fr | 0.1 | 0.1 | Frame fraction area
H_B | 1 | 1 | Height/Breadth of the windows
A1_deg | 18 | 18 | Angle of symmetric lateral screens [deg]
A2_deg | 30 | 70 | Angle of top screen [deg]
A3_deg |  |  | Angle of frontal screen [deg]
D_H |  |  | Distance/Height of frontal screen

## general comments
parameters | value
azimuth_12h_deg | 180 | Azimuth of the orientation named 12h [deg]
h_ceiling_m | 2.74 | Ceiling height [m]
n_infiltr_per_h | 0 | Air infiltration rate [1/h]
internal_blind | 0 | Presence (1) / absence(0) of internal blind
suspended_ceiling | 1 | Presence (1) / absence(0) of suspended ceiling
raised_floor | 0 | Presence (1) / absence(0) of raised floor
carpet | 1 | Presence (1) / absence(0) of carpet
month | 7 | Number of the month for the simulation
t_in_C | 26 | Internal temperature set point [°C]
t_adj_C | 30 | Temperature of adjacent unconditioned spaces [°C]
plant_start_h | 7 | Start time of the air conditioning system
plant_stop_h | 23 | Stop time of the air conditioning system
occ_start_h | 7 | Start time of the occupancy
occ_stop_h | 23 | Stop time of the occupancy
occ_rad_W | 60 | Radiative heat gains per occupant
occ_conv_W | 30 | Convective heat gains per occupant
appliances_Wm2 | 10 | Convective heat gains from appliances
lighting_rad_Wm2 | 2.4 | Radiative heat gains from the lighting system
lighting_conv_Wm2 | 2.4 | Convective heat gains from the lighting system
lighting_factor | 0.8 | Reduction factor of lighting heat gains due to air exhaust through the luminaires
roof_factor | 0.7 | Reduction factor of roof transmission heat gains due to air exhaust plenum in the suspended ceiling
alpha_wall | 0.6 | Short wave absortion factor of external walls surface
alpha_roof | 0.9 | Short wave absortion factor of the roof surface
opaque_wall_shading | 0 | Presence (1) / absence(0) of shading on the exteranl walls and on the roof